[image: image8.emf]PARLIAMENT HOUSE - TOTAL ENERGY CONSUMPTION

0

50

100

150

200

250

300

350

1988/19891989/19901990/19911991/19921992/19931993/19941994/19951995/19961996/1997 1997/19981998/19991999/20002000/20012001/20022002/20032003/20042004/20052005/2006

FINANCIAL YEAR

ENERGY CONSUMPTION (TJ)

Electricity

Gas

 Parliament of Australia

[image: image9.emf]ELECTRICITY CONSUMPTION AND CHARGES

5

10

15

20

25

30

35

40

45

50

1988/1989 1989/1990 1990/1991 1991/1992 1992/1993 1993/1994 1994/1995 1995/1996 1996/1997 1997/1998 1998/1999 1999/2000 2000/2001 2001/2002 2002/2003 2003/2004 2004/2005 2005/2006

FINANCIAL YEAR

CONSUMPTION (GWhr)

0.0

0.5

1.0

1.5

2.0

2.5

3.0

3.5

4.0

4.5

COST (MILLIONS)

Consumption Cost

 Department of Parliamentary Services  

Parliament House 2005-2006 Environmental Performance Report

Introduction

1 The information in this report is structured using the core Global Reporting Initiative (GRI) environment performance indicators as a framework. The Global Reporting Initiative is an independent institution whose mission is to develop and disseminate globally applicable Sustainability Reporting Guidelines. These Guidelines are for voluntary use by organisations for reporting on the economic, environmental and social dimensions of their activities, products and services.
Materials

EN 1 Total materials use other than water, by type

2 Parliament House uses a variety of materials for the efficient functioning of Parliament. Some of the major items that have an impact on the environment are paper, fertiliser and chemicals. The number of separate organisations occupying Parliament House and the diverse functions performed by them make it impossible to gather accurate data against this indicator.

3 The purchase of technology by the Department of the Senate focussed on minimising resource consumption, including power, the reusability and recycling of equipment at the end of its life, and having suppliers take back packaging for reuse or recycling. Similar considerations were built into the selection criteria for the standing offer for desktop computer equipment for the Parliament which is now in operation.
4 In the Department of the House of Representatives ‘Green purchasing’ formed an integral part of purchasing selection criteria and was used for major purchases including chairs, refrigerators, dish washers and fax machines. Elements such as energy consumption, sustainable manufacturing techniques, the reuse of parts on obsolete equipment and the return of packaging were included.

EN 2 Percentage of materials used that are wastes (processed or unprocessed) from sources external to the reporting organisation.

5 In 2005-2006 Parliament House did not use any significant quantity of materials that are wastes from sources external to the organisation.

Energy

EN 3 Direct energy use segmented by primary source.

6 The main components of energy use in Parliament House are gas and electricity. Gas is used for heating, domestic hot water and catering equipment. Electricity is used to provide a variety of services including office lighting, power, mechanical services, lifts, chillers, computer equipment, catering equipment, water features, central waste plant and boosted hot water heating.
7 Each year Parliament House reports its energy consumption to the Australian Greenhouse Office as part of the report on Energy Use in the Australian Government’s Operations. In 2005-2006 Parliament House consumed the following energy:

	Parliament House Building
	

	Electricity (kWh) 
	23,244,060

	Natural Gas (GJ) 
	47,307

	Diesel (Generators & Boilers)(L) 
	11,445

	Greenpower (kWh) 
	2,853,996

	Total GJ 
	141,702

	Area (m²) 
	152,000

	MJ/Area (m²)/annum 
	932

	
	

	West Block Office - Tenant Light and Power
	

	Electricity (kWh) 
	304,490

	Greenpower (kWh) 
	26,477

	Total GJ 
	1,191

	Occupancy (People) 
	4

	Area (m²) 
	2,294

	MJ/Occupancy (People)/annum 
	27,709

	MJ/Area (m²)/annum 
	519

	m²/person 
	53.35

	
	

	Passenger Vehicles
	

	LPG (L) 
	3,954

	Petrol (L) 
	76,608

	Automotive Diesel (L) 
	0

	Total GJ 
	2,722

	Distance Travelled (km) 
	1,011,251

	MJ/Distance Travelled (km)/annum 
	2.69

	
	


	Other Transport – Truck, Gardening Equipment & Forklifts
	

	Automotive Diesel (L) 
	8,856

	LPG (L) 
	1,880

	Petrol (L) 
	3,225

	Total GJ 
	500

	
	


Summary

	Component
	Energy Consumption (GJ)
	Cumulative Total (GJ)

	Parliament House Electricity
	93,953
	93,953

	Parliament House Gas
	47,307
	141,260

	Parliament House Diesel
	442
	141,702

	West Block Light and power
	1,191
	142,893

	Passenger Vehicles
	2,722
	145,615

	Truck, Gardening Equipment & Forklifts
	500
	146,115

	TOTAL
	146,115
	146,115


Performance Overview

8 The primary energy used within Parliament House during the 2005-2006 reporting year (electricity and gas) was 141,260 GJ, which is 5.8% higher than the energy consumption in 2004-2005. The reasons for the increase were:
(a) There were more sitting days in 2005-2006 (because 2004-05 included an election period).

(b) DPS took on responsibility for street lighting around Parliament Drive.
(c) The Recreation Centre refurbishment was completed and the centre reopened from 1 August 2005. This meant that the swimming pool plant and air conditioning system contributed to the building load from then.

(d) The installation of compressors to operate the new security bollards.

(e) the lifting of water restrictions in Autumn 2005, when water features around Parliament House were turned on again resulted in increased electricity consumption. If level three water restrictions are introduced again during the 2006-07 summer, electricity consumption will again reduce.

(f) one of the coldest autumns since 1967 resulted in an increase in gas consumption.

9 In 2005-2006 Parliament House purchased 2,853,996 kWhrs of green energy from the Snowy Hydro scheme. This represents 10.9% of total electricity consumption in 2005-2006.

10 In 2005-2006 DPS negotiated a new electricity contract that will come into effect on 1 July 2006. The new electricity contract will see 10% of Parliament House’s electricity being sourced from ‘new’ green energy sources including wind and solar and 15% being sourced from ‘old’ hydro produced green electricity. In total, 25% of Parliament House’s electricity supply will be sourced from renewable energy sources.
11 DPS is reviewing the energy strategy to reduce long-term energy use and greenhouse gas emissions. The strategy is expected to be completed in 2006-07.
12 Since Parliament House was opened in 1988, DPS has achieved the following results over the 1988–89 baseline year. 

(a) Electricity reduction of 40%;
(b) Gas reduction of 73%;
(c) Carbon dioxide emission equivalent reduction of 45%; and
(d) Total energy consumption reduction of 58%.
13 DPS complied with all the applicable requirements of the Government’s policy for improving energy efficiency in Commonwealth Government operations. Details can be found on the environmental portal accessible from the Parliament House web site at http://www.aph.gov.au/dps
14 The reduction in energy consumption is shown in the following graph.

[image: image10.emf]GAS CONSUMPTION AND CHARGES

20

40

60

80

100

120

140

160

180

200

1988/19891989/19901990/19911991/19921992/19931993/19941994/19951995/19961996/19971997/19981998/19991999/20002000/20012001/20022002/20032003/20042004/20052005/2006

FINANCIAL YEAR

CONSUMPTION (TJ)

0.0

0.2

0.4

0.6

0.8

1.0

1.2

1.4

1.6

1.8

COST (MILLIONS)

Consumption Cost


Electricity Consumption

15 Electricity consumption during 2005-2006 was 26,098,056 kWhrs, an increase of 3% compared with 2004-05. Electricity consumption is approximately 40% higher on a sitting day compared with a non-sitting day. As noted above, there were more (27) sitting days in 2005-06 than in 2004-05.
16 When compared with 2003-2004 (a year with a more typical sitting pattern) electricity consumption decreased by 6%.
[image: image11.emf]PARLIAMENT HOUSE - TOTAL CARBON DIOXIDE EMISSIONS

10

20

30

40

50

60

1988/1989 1989/1990 1990/1991 1991/1992 1992/1993 1993/19941994/1995 1995/1996 1996/1997 1997/1998 1998/1999 1999/20002000/2001 2001/2002 2002/2003 2003/2004 2004/2005 2005/2006

FINANCIAL YEAR

CARBON DIOXIDE (KTonnes)

Savings due

to Purchase

of Green

Energy

Electricity

Gas


Gas Consumption 

17 The increase in sitting days also contributed to higher gas costs. Gas consumption during 2005-06 was 47,307 GJ, an increase over 2004-05 of 11.8%.
18 Gas consumption is approximately 35% higher on a sitting day compared with a non-sitting day and, as noted earlier, there were 27 more sitting days in 2005-06.

[image: image12.emf]PARLIAMENT HOUSE - TOTAL ENERGY CONSUMPTION

0

50

100

150

200

250

300

350

1988/19891989/19901990/19911991/19921992/19931993/19941994/19951995/19961996/1997 1997/19981998/19991999/20002000/20012001/20022002/20032003/20042004/20052005/2006

FINANCIAL YEAR

ENERGY CONSUMPTION (TJ)

Electricity

Gas


EN 4 Indirect energy use.

19 Indirect energy refers to the total amount of energy used to provide electricity to Parliament House and includes the energy used to produce and transmit the electricity to Parliament House. In 2005-2006 most of Parliament House’s electricity came from coal fired power stations with 10% ‘old’ green energy being purchased from the Snowy Hydro scheme.
20 For 2005-2006 the figures used to calculate indirect energy were based on the National Greenhouse Gas Inventory 2002 Table 4-19 published by the AGO.
21 Based on this factor indirect energy consumption for Parliament House in 2005-2006 was 253,526 GJ.

Water

EN 5 Total water use

22 Water consumption for 2005-2006 was 268,470 kL. This represented a 38% increase in water consumption compared with the 2004-2005 financial year.

23 This significant increase was due to the following factors:

(a) A considerable amount of landscape redevelopment work was undertaken in 2005-06 following completion of the security enhancement project, and also replanting of trees, shrubs and turf following the drought. The new plantings required considerably more water than established plants. The work undertaken included:

(i) laying 1.6 ha of turf; 
(ii) seeding 0.9 ha of lawn in spring; 
(iii) laying 2,000 m2 of buffalo turf; 
(iv) planting 2,500 trees and shrubs as part of the replacement following the drought; and

(v) establishing 10,134 plants on the Senate, House of Representatives and Ministerial access road banks.
(b) The Australian Capital Territory experiencing a very dry period from December 2005, with a total evaporation loss of 1,082 mm during the seven months from 1 December (based on rainfall and evaporation data from the Bureau of Meteorology). The long-term average for that period is 793 mm.
(c) A fault with the irrigation system, and a burst irrigation main that ran for two and a half hours before isolation, resulted in excessive water consumption.
(d) Most of the 21 water features around Parliament House were turned off in 2004-2005 because of water restrictions and the water display upgrade project. The swimming pool and spa were also closed due to refurbishment. In 2005-2006 the water features and pool were fully operational again resulting in increased water consumption due to backwashing and evaporation from these water features and pools.
(e) Water consumption for toilet facilities, catering facilities and air conditioning plant is higher on sitting days due to an increased building population and operating hours. There were 27 additional sitting days in 2005-2006 compared with 2004-2005 resulting in an increase in water consumption.

24 As part of the Recreation Centre upgrade project new dual flush toilets and five waterless urinals were installed in the male change rooms.
25 A second waterless urinal system using microbial bacteria cubes was trialled in three urinals in the private areas of Parliament House. The observed results included no deterioration in the presentation of urinals, no visible build up of crystalline uric acid or sulphate discolouration in pipework and no unpleasant odours. The results of this trial are being added to work being undertaken by consultants—analysing the range of reduced flow or waterless urinals now available in Australia—prior to a decision being made on which technology to implement throughout the rest of the 62 male toilet facilities in the building. 

26 The consumption of water can be broken down into the following categories.

[image: image1.emf]Parliament House 2005-2006 Water Consumption Breakdown (kL)

Flushometer 21,540

Cooling Tower 19,063

Fire Hose Reels 169

Domestic Hot water 9,068

Building Other 43,442

Irrigation 175,188


27 The following graph shows the consumption of water since the building was opened in 1988.

[image: image2.emf]Parliament House Water Consumption

251,326

325,476

476,908

429,886

324,924

304,263

308,222

349,451

238,519

207,461

212,725

222,368

255,538

285,745

277,709

238,164

194,694

268,470

0

100,000

200,000

300,000

400,000

500,000

600,000

1988-891989-901990-911991-921992-931993-941994-951995-961996-971997-981998-99 1999-20002000-012001-022002-032003-042004-052005-06

Financial Year Ending 30 June

Water Consumption (kL)


Biodiversity

EN 6 Location and size of land owned, leased, or managed in biodiversity-rich habitats

28 In 2005-2006 DPS did not own or lease any land in biodiversity rich habitats.

EN 7 Description of the major impacts on biodiversity associated with activities and/or products and services in terrestrial, freshwater, and marine environments

29 In 2005-2006 there were no major impacts on biodiversity associated with activities and/or products and services in terrestrial, freshwater, and marine environments.
Emissions, Effluents and Waste

EN 8 Greenhouse gas emissions

30 DPS is a member of the Greenhouse Challenge Program and has been reporting on greenhouse gas emissions from Parliament House since 1997. 




31 The following is an extract from the 2005-2006 Greenhouse Challenge report. 

	 
	Consumption
	Emissions (tonnes CO2 -e)

	Emissions

	Stationary energy

	 
	Electricity
	26,098,056
	kWh
	27,528

	 
	Natural gas
	47,307
	GJ
	3,373

	 
	Automotive diesel
	11
	kL
	34

	Transport energy

	 
	Automotive diesel
	9
	kL
	27

	 
	Automotive gasoline (Petrol)
	80
	kL
	222

	 
	LPG
	6
	kL
	10

	Waste to landfill

	 
	CO2-e
	494
	tonnes
	494

	Total for emissions
	31,688

	Offsets

	Stationary energy

	 
	Greenpower
	2,853,996
	kWh
	(3,010)

	Nett inventory for FY2005-2006
	28,678



32 The following table shows greenhouse gas emissions due to Parliament House electricity and gas consumption in the 2005-2006 financial year.
	Source
	Emissions (tonnes CO2 -e)

	Electricity
	27,528

	Natural Gas
	3,373

	Greenpower
	(3,010)

	 
	27,891


33 The following graph shows annual greenhouse gas emissions from the Parliament House electricity and gas consumption since the building was opened in 1988.

[image: image13.emf]PARLIAMENT HOUSE - TOTAL CARBON DIOXIDE EMISSIONS

10

20

30

40

50

60

1988/1989 1989/1990 1990/1991 1991/1992 1992/1993 1993/19941994/1995 1995/1996 1996/1997 1997/1998 1998/1999 1999/20002000/2001 2001/2002 2002/2003 2003/2004 2004/2005 2005/2006

FINANCIAL YEAR

CARBON DIOXIDE (KTonnes)

Savings due

to Purchase

of Green

Energy

Electricity

Gas


34 Greenhouse gas emissions due to the consumption of electricity and natural gas for the 2005-06 financial year was 27,891 tonnes of CO2. This represents a 4.3% increase in total greenhouse gas emissions compared with the 2004-2005 Financial Year.

EN 9 Use and emissions of ozone depleting substances

35 The ozone depleting substances used at Parliament House are refrigerants which are used in:

(a) chillers which provide cooling for the building’s air conditioning; 

(b) coolrooms;

(c) freezers; and

(d) refrigerators.

36 The table below shows the refrigerants that were used in 2005-2006 and the Ozone Depletion Potential for each of these of these refrigerants.

	Refrigerant
	Qty Used (kg)
	Ozone Depletion Potential
	CFC-11 equivalent (kg)

	404A
	104
	0
	0

	R22
	48
	0.055
	2.64

	R134a
	0
	0
	0

	Total
	152
	
	2.64


EN 10 NOx, SOx, and other significant air emissions by type

37 The combustion of natural gas for heating, hot water and cooking purposes generates quantities of NOx, SOx, and other air emissions from Parliament House. Each year Parliament House reports on these emissions to the National Pollution Inventory. The following table lists the emissions from Parliament House for 2005-2006.

	Substance
	Total Emissions (kg)

	Carbon monoxide
	1,800

	Oxides of nitrogen
	1,900

	Particulate matter (PM10)
	170

	Total Volatile organic compounds
	120

	Sulfur dioxide
	11

	Polycyclic aromatic hydrocarbons
	0.0150


EN 11 Total amount of waste by type and destination

Waste to Landfill
38 Waste to landfill includes all the waste sent to landfill from the operations of Parliament House. It does not include waste generated from large projects such as the security wall.

39 In the 2005-2006 financial year the amount of waste sent to landfill was 475 tonnes.
[image: image4.emf]Waste to Landfill

584

646

645

625

610

644

482

475

0

100

200

300

400

500

600

700

1998-99 1999-2000 2000-01 2001-02 2002-03 2003-04 2004-05 2005-06

Years

Tonnes


Recycled Waste

40 Recycled Waste includes recycled paper, recycled cardboard, classified paper waste, commingled waste, printer cartridges, lamps, used oil, grease and batteries. It does not include any landscape or construction waste that is recycled.

41 Paper recycling rates continued to improve, with 345 tonnes of paper and cardboard being diverted from landfill in 2005-06. A waste audit conducted in 2005 identified that Parliament House is recycling 63% of available paper and cardboard. 

[image: image5.emf]Paper Recycled

0

50

100

150

200

250

300

350

400

1998-99 1999-2000 2000-01 2001-02 2002-03 2003-04 2004-05 2005-06

Years

Tonnes


42 Printer cartridge recycling resulted in 1,736 kg (an increase of approximately 400 kg) of toner cartridges being recovered and recycled from Parliament House. Cartridge recycling opportunities in electorate offices saw 2,454 kg of cartridges being recovered and recycled (an increase of approximately 50 kg). This resulted in a total of 4.19 tonnes of cartridge materials being removed from the waste stream over the reporting year. 
[image: image6.emf]Cartridge Recycling

0

500

1000

1500

2000

2500

3000

3500

4000

4500

2003-04 2004-05 2005-06

Financial Year

Kilograms

Electorate Offices

Parliament House


43 The recycling of 28,000 lamps, grease, used oil, metals and batteries, glass and some commingled material added to the Parliament’s recycling results.

Landscape Waste

44 Landscape waste disposed of to landfill or recycled is separately recorded and monitored.

45 In 2005-2006, 3,429 tonnes of landscape waste was generated from maintenance activities in the Parliament House landscape. 99.74% of this landscape waste was recycled. Returfing of the grassed ramps at the southern end of the building resulted in 3,075 tonnes of grass and soil being recycled by a local golf course, at no cost to the Parliament. The short distance travelled by trucks removing the material limited diesel consumption and the contribution to greenhouse gas production.

46 Trends over time can be seen in the following graph.

[image: image7.emf]Landscape Waste

0

500

1,000

1,500

2,000

2,500

3,000

3,500

4,000

1998-99 1999-

2000

2000-01 2001-02 2002-03 2003-04 2004-05 2005-06

Years

Tonnes

Total

Landscape

Waste

Waste to

Recycling

Landscape

Waste to

Landfill


EN 12 Significant discharges to water by type

47 In a typical year approximately 62.8 ML is discharged into the sewerage system. The sewerage is essentially domestic strength. There are a number of installed systems to prevent trade waste from entering the sewerage system. These include:

(a) Grease traps on all of the kitchens (which are cleaned out every 3 months);

(b) A coalescing plate filter on the vehicle washdown bay (to prevent oil from entering the sewer); and

(c) A system to remove paint solids from paint brush washing facilities before they enter the sewer.
48 There was no measurable leachate runoff from the site into the surrounding waterways during the reporting period.

EN 13 Significant spills of chemicals, oils, and fuels in terms of total number and total volume

49 In 2005-2006 there were no significant spills of chemicals, oils and fuels from Parliament House.

50 Procedures are in place to minimise the risk of such incidents occurring and necessary materials are maintained in strategic areas throughout the parliamentary precincts to manage such an incident should it occur. 

Products and Services

EN 14 Significant environmental impacts of principal products and services

51 In 2005-2006 Parliament House did not produce any products or services that had significant environmental impacts.

EN 15 Percentage of the weight of products sold that is reclaimable at the end of the products’ useful life and percentage that is actually reclaimed

52 In 2005-2006 Parliament House did not sell any products that are reclaimable at the end of the product’s useful life.
Compliance

EN 16 Incidents of and fines for non-compliance with all applicable international declarations/conventions/treaties, and national, sub-national, regional, and local regulations associated with environmental issues.

53 In 2005-2006 there were no instances of fines for non compliance with any regulations associated with environmental issues.
� EMBED MSGraph.Chart.8 \s ���





� EMBED MSGraph.Chart.8 \s ���





� EMBED MSGraph.Chart.8 \s ���





� EMBED MSGraph.Chart.8 \s ���








� this figure has been recalculated since publication of the Annual Report





	


	Parliament House

Canberra ACT 2600

Telephone: (61) 02 6277 7111
	ABN 52 997 141 147


14
Annual Environmental Report 2005-06 05.doc

[image: image14.emf]ELECTRICITY CONSUMPTION AND CHARGES

5

10

15

20

25

30

35

40

45

50

1988/1989 1989/1990 1990/1991 1991/1992 1992/1993 1993/1994 1994/1995 1995/1996 1996/1997 1997/1998 1998/1999 1999/2000 2000/2001 2001/2002 2002/2003 2003/2004 2004/2005 2005/2006

FINANCIAL YEAR

CONSUMPTION (GWhr)

0.0

0.5

1.0

1.5

2.0

2.5

3.0

3.5

4.0

4.5

COST (MILLIONS)

Consumption Cost

[image: image15.emf]GAS CONSUMPTION AND CHARGES

20

40

60

80

100

120

140

160

180

200

1988/19891989/19901990/19911991/19921992/19931993/19941994/19951995/19961996/19971997/19981998/19991999/20002000/20012001/20022002/20032003/20042004/20052005/2006

FINANCIAL YEAR

CONSUMPTION (TJ)

0.0

0.2

0.4

0.6

0.8

1.0

1.2

1.4

1.6

1.8

COST (MILLIONS)

Consumption Cost

[image: image16.png]


_1219035930

_1219042117

_1219043403

_1219035801

